## PCB Disposal Checklist 2016
Appendix A - PCB Oil and Contaminated Equipment Removal Checklist
Grip stage | Action required | Tick when complete
Grip 1-4 | Check with Route Asset Manager (E & P) to confirm if the equipment for removal is listed on the Network Rail PCB register. Inclusion of equipment on this register means that no further oil testing is required and that the oil shall be treated as PCB contaminated and disposed of by high temperature incineration at a licensed site. Contractual arrangements between Network Rail and the principal contractor and between the principal contractor and subcontractors must preclude any other means of disposal. If the equipment is not listed on the Network Rail PCB register or if there is any doubt about PCB contamination, the Project Manager shall commission a competent contractor to undertake survey and analysis work to establish if PCB contaminated oils are present within equipment to be removed. Any equipment confirmed as contaminated by PCB oil at or above 50ppm PCBs shall be reported to Network Rail Route asset manager (E & P) to update the Network Rail PCB register.
Grip 1-4 | Check oil samples for PCB testing will be treated as hazardous waste using hazardous waste consignment note, premises code and unique reference to the equipment they relate to (e.g. equipment serial number).
Grip 1-4 | Check that the GRIP environmental appraisal, environmental action plan and ITT environmental information and requirements products contain all relevant information about PCB oils and contaminated equipment so that contractors are aware e.g. size, weight, oil volumes and PCB levels.
Grip 1-4 | Check that the contract makes explicit reference to the disposal of PCB contaminated waste and the need for the Principal Contractor to show that competent contractors will be used for the disposal of PCB contaminated waste.
Grip 4-8 | Check contractors EMP, complete GRIP Works EMP acceptance form and GRIP SWMP acceptance checklist. Only accept these plans if the disposal of PCB waste has been adequately addressed using licensed contractors and disposal sites permitted to accept wastes containing PCBs.
Grip 4-8 | Check contractors EMP contains a risk assessment confirming the intended method of removal of PCB oil from oil filled equipment i.e. drain oil on site or removal of the whole piece of equipment intact and drain off site.
Grip 4-8 | Check the contractor’s Works EMP contains the following key milestones: Dilapidation survey Obtaining oil samples for PCB testing Confirmation of PCB test results Equipment de-commissioning Draining of waste oil Removal of oil from site Removal of redundant equipment from site Check dilapidation survey includes a requirement to establish the quantity of oil in the equipment at the time the site is handed over to the contractor. Include requirement to record this on the dilapidation form and back up by photos of sight glass if possible. Check a lock has been applied to the equipment drain valves to prevent them being opened.
Grip 4-8 | Check contractor has obtained a valid hazardous waste premises code and prepared consignment notes in advance.
Grip 4-8 | Check contractor’s arrangements for supervising the draining of oil from equipment, its removal from site and the security of the waste on site.
Grip 4-8 | Ask contractor what checks they make to confirm that the equipment (e.g. transformers) contain oil and how PCB analysis results are passed to contractors and actioned accordingly e.g. how the PCB contaminated waste oil (at or above 50ppm) is kept separate from the non PCB contaminated waste oil so that mixing of the two types is prevented.
Grip 4-8 | Check contractor has a process in place to check consignment notes are signed and completed correctly before waste leaves premises (e.g. nominated representative from Principal contractor on site to supervise disposals, check and sign consignment notes). Process must prevent waste leaving site if paperwork is incomplete or incorrect and Network Rail project team representative should also be present.
Grip 4-8 | Check contractors work package plans and task briefing sheets contain an acceptable method of working with regard to disposal of PCB oil and decontamination of PCB contaminated equipment.
Grip 4-8 | Carry out spot check PGI to check contractor waste disposal arrangements.
Grip 4-8 | For equipment on the Network Rail PCB Register the Project Manager should obtain copies of the completed consignment notes and certificates of destruction confirming disposal of the PCB contaminated waste oil and send them to the Route Asset Manager (E &P).
Grip 4-8 | Retain and store copies of the fully completed consignment notes on the project and H & S files for at least three years.
Inspection by and signature