## Slide 1
Electrical Power Distribution Safety Hour
Access into traction and non-traction distribution locations
Version 1 March 2019

## Slide 2
Contents
Section 1 – Safety Hour:
Introduction and purpose of the session
Overview of the incident at Godinton Substation in December 2018
Accessing distribution locations Discussion topics
Arc Flash PPE
Section 2 – Sentinel Competence Re-brief:
Re-briefing on the Safety Requirements for Accessing Distribution sites (mandatory for all Level A, B, C competence holders)
Where you see this icon at the top of slide, it denotes a team discussion

## Slide 3
Section 1:
Safety Hour

## Slide 4
Introduction and Purpose
Following a serious safety incident at Godinton DC traction substation in December 2018, this safety hour has been produced to share key learning from the incident.
It is targeted at all holders of DIST Level A, B or C competence within Network Rail and contractors organisations i.e. people that take a lead safety role when accessing or working in traction and/or non traction distribution locations.
The learning from this safety hour should be applied to all traction and non-traction distribution locations regardless of electrification type.
A formal re-briefing of the safety requirements when accessing traction and non-traction distribution locations is contained as part of this safety hour. This needs to be recorded in Sentinel prior to 29th July 2019 in order to maintain your DIST Level A, B or C competence.

## Slide 5
What actions would you take if you discovered the environment in a distribution location wasn’t normal?
Godinton Incident
Members of the Distribution & Plant team were responding to a fault where a dc circuit breaker had failed to reclose following a tripping.
Upon arrival, steam was reported to be present inside the DC substation.
How do you and your team respond to situations involving faults?
Describe what could happen if steam or condensation is present in a distribution location?

## Slide 6
Godinton Incident
What could be the consequences of an electrical flashover?
Once the steam had dissipated, an attempt was made to replace a blown 750V 2A DC fuse within the 750V DC switchboard. An electrical flashover occurred as a result.
Our colleague suffered serious injuries from the flashover.
The substation and other parts of the traction power system nearby were substantially damaged by the fire that resulted.
An investigation is on-going

## Slide 7
Godinton Incident Discussion
What have you heard about Godinton and what were your initial thoughts, concerns? What have you learnt?
If you felt unsure when asked to access a distribution substation would you say so? How do you feel about challenging and being challenged?

## Slide 8
What do you think may stop us from challenging either ourselves, colleagues, managers or our contractors?
A challenging discussion….
‘…we’ve got to get this job done quickly to get trains moving…’
‘…just need to get the job done or my manager will not be happy…’
‘…what’s the point…I raised this before but nothing was done about it…’
‘…they have got a lot more experience than me, I don’t want to sound stupid…’
‘…if we just get the task done we can get back on time…’
‘…we were OK when we did it like this last time…’

## Slide 9
What do you think are the benefits of challenging when a situation arises?
What might happen if you don’t challenge or raise your concern ?
Challenge may feel hard, but don’t let it…
At Network Rail we encourage it….

## Slide 10
How can we help each other to make the challenge and also respond to challenge? What might we say differently?
Helping us to challenge ….
‘…yes we have to get the job done, but only if it is safe to do so…’
‘…I need to tell my manager its just not feeling safe or right…’
‘…I will keep raising this until it’s sorted…’
‘…no question is a stupid question, it could save a life…’
‘…if we need more time to do the job safely we need to raise this…’
‘…we might have been OK last time, but this looks different…’

## Slide 11
Accessing distribution locations
What have you understood from the national safety bulletin?
How do the requirements affect your teams or method of work?
Following the findings from the Godinton incident, a national safety bulletin was issued in January 2019.
Link to National Safety Bulletin NRB 19/01

## Slide 12
Discussion 1
What would you tell them to make sure they are safe?
Picture a scenario where you are about to take someone under your care, or maybe a new starter who has never been on the railway infrastructure before, into a traction or non-traction distribution location

## Slide 13
Discussion 2
What do you think are the personal factors that should also be checked before accessing or undertaking a task in a distribution location?
What do you need to know before you enter - who could tell you?

## Slide 14
Discussion 3
What hazards should you be aware of when entering a distribution location?
What actions would you take if any of these conditions are present?

## Slide 15
Arc Flash PPE
Following the Godinton incident, the minimum requirements for Arc Flash PPE have been enhanced.
Consider as 3 layers of clothing – base layer (underclothes), main layer, and outer layer
Distribution and Plant maintenance and projects staff who undertake work inside traction / non traction distribution locations will be required to wear the following at all times:
  Main layer - Arc Flash polo shirt and Arc flash cargo trousers
  Any Base layer underclothes MUST be either natural 100% cotton or approved flame retardant items
Note if you are only a DIST Level C you cannot work on the distribution equipment and so are not mandated to wear the Arc Flash PPE
Main Layer – polo shirt and cargo trousers
Base Layer refers to 100% cotton undergarments or approved flame retardant items

## Slide 16
Arc Flash PPE
Outer layer - Certain activities require additional Arc Flash PPE such as a jacket, over-trousers, gloves, balaclava and visor.
Typical examples of these activities are:
Racking in and out dc open-frame circuit breakers
Application of portable earthing equipment on 25 kV VCB busbars and circuit terminations
This outer layer Arc Flash PPE must be worn as well as the Arc Flash polo shirts and cargo trousers.
Task Risk Control Sheets and work instructions are being updated to reflect where enhanced Arc Flash PPE is mandated.
Outer Layer – including jacket, overtrousers, gloves, balaclava, visor

## Slide 17
What activities and tasks do you do in a substation?
What Arc Flash PPE do you need for these?
Arc Flash PPE discussion
Click on this link to Network Rail Yammer Group for PPE - includes Arc Flash PPE Catalogue and demo of Arc Flash PPE

## Slide 18
Use your SENSES…
Appearing at notice board near you….
… a reminder of the requirements when accessing a distribution location, think of your SENSES….

## Slide 19
SUBSTATION
ENTRY
NOISE
SMELL
ENVIRONMENT
SAFETY
All traction and HV non-traction locations (includes Substations, TP Huts, Switching Stations, Feeder Huts, all 25kV and Autotransformer substations)
No access unless competent and authorised
Listen for abnormal noises such as crackling or hissing as these could indicate electrical breakdown of the components
Be aware of abnormal smells such as burning, ozone (electrical discharge), rotten eggs (Arc’ed SF6 discharge)…
Look for signs of water ingress, condensation, burning, smoke…
A safe system of work must be in place and the required arc flash PPE worn for the task to be undertaken

## Slide 20
If you are unsure…STOP….DO NOT work if it’s not safe…

## Slide 21
Section 2:
Sentinel Re-brief
Access into Traction / Non Traction Distribution Locations

## Slide 22
Contents
Section 2 - Sentinel Re-brief for Access into Traction / Non Traction Distribution Locations
Purpose of the session
Scope
Hazards
Be Aware and Act
Procedure Reminder
Arc Flash PPE
Discussion points
Feedback and contact
Where you see this icon at the top of slide, it denotes a team discussion

## Slide 23: Access into Traction / Non Traction Distribution Locations - Purpose
Following a serious safety incident at Godinton DC traction substation in December 2018, we require that all personnel who hold the following competences:
Level C DIST,
Level B DIST (ACi, ACi+DCi),
Level A DIST
…undertake this re-briefing of the safety requirements from the current DIST level C competence to reinforce understanding of the safety risks when accessing traction and non traction distribution locations.
This briefing has been set up as a Sentinel competence event (LC DIST REBRIEF) and must be recorded by your Sentinel Sponsor before 29th July 2019 in order to retain your Level A, B or C competence.

## Slide 24: DIST Level C Re-briefing - Scope
The Level C competence (in accordance with NR Standard NR/L2/CTM/018) covers the requirements and procedure when accessing and egressing a traction or non-traction distribution location (such as DC substations, 25 kV Feeder Stations, Track Paralleling Huts, 6.6 kV substations, etc..).
Note: the distribution location also includes the compound and the electrical distribution equipment installed within it.
The Level C competence alone does not allow work to be carried on any of the equipment inside the distribution location, it is solely for access and egress.
Where work is required to be undertaken on the equipment, the individual shall either hold a higher competence such Level B or Level A, or the specific equipment competence (such as Network Rail telecoms staff working on the modem / communications equipment)

## Slide 25: DIST Level C Re-briefing - Hazards
When entering a distribution location you must be aware of the potential hazards such as:
Asbestos components
If damage to asbestos material is suspected, arrangements must be made to immediately leave and secure the building. The ECO must be informed accordingly and the asbestos risk reported to your line manager.
Damage to Asbestos Containing Materials must be reported to the Operational Property Help Desk (OPHD) on 0845 873 1289

## Slide 26: DIST Level C Re-briefing - Hazards
When entering a distribution location you must be aware of the potential hazards such as:
Exposed Electrical Equipment
(such as batteries & connections)
Access to or near equipment with exposed live terminals shall be avoided unless the individual also holds the specific equipment competence and has complied with the relevant task risk controls.

## Slide 27: DIST Level C Re-briefing - Hazards
When entering some sub surface distribution locations you must be aware of the potential hazards such as:
Fire Suppression systems
(such as automatic gas (CO2) discharge systems)
(With permission from the ECO where applicable) An automatic system must be isolated at the control panel adjacent to the door prior to entering the location, and re-activated prior to departure.

## Slide 28: DIST Level C Re-briefing – be aware and act
When entering a distribution location it is extremely important to remain vigilant and alert to changes in the environmental conditions inside.
Changes in environmental conditions can include:
    Crackling or hissing noises
    Smells (such as burning, ozone or rotten eggs)
    Smoke
    Water ingress, steam or significant condensation

## Slide 29
  Crackling or hissing noises
  This can be the indication of electrical discharge and/or the breakdown of the electrical equipment which may lead to hazardous / lethal voltages appearing on metalwork or present an explosion risk.
  If this is detected, the distribution location must be immediately evacuated and the ECO contacted via suitable means other than the substation phone.
DIST Level C Re-briefing – be aware and act

## Slide 30
    Smells (such as burning or ozone)
    This can be the indication of electrical discharge and the breakdown of components of the electrical equipment which may lead to hazardous / lethal voltages appearing on metalwork or present an explosion risk.
    Rotten Eggs
    This is associated when an fault has occurred within SF6 filled equipment and has led to a breakdown of the SF6 gas components.
    There may also be evidence of a white ash like material.
    Do not touch.
    If any of the above is detected, the distribution location must be immediately evacuated and the ECO contacted via suitable means other than the substation phone.
DIST Level C Re-briefing – be aware and act

## Slide 31
    Smoke
    This can be the indication of overloaded electrical equipment, flash over and the breakdown of the electrical equipment which may present a fire/explosion risk.
    If the above is detected, the distribution location must be immediately evacuated and the ECO contacted via suitable means other than the substation phone.
DIST Level C Re-briefing – be aware and act

## Slide 32
  Water ingress (Steam) or significant condensation
  Evidence of water ingress (Steam) or significant condensation on electrical equipment will increase the risk of electrical discharge and flash-over.
  Actions shall be taken in accordance with national safety bulletin NRB 19/01.
  If steam is detected, the distribution location must be immediately evacuated and the ECO contacted via suitable means other than the substation phone.
  The Electrification & Plant Maintenance Engineer must also be contacted and Route Control advised.
DIST Level C Re-briefing – be aware and act

## Slide 33
Building Fabric - Water ingress, defects with doors, damage to windows
The general condition of the building should be reviewed and any defects with the building that could lead to water ingress or a reduction in the buildings security should be reported.
If the above are detected, these shall be reported to the Operational Property Help Desk (OPHD) on 0845 873 1289.
Please also ensure that the ECR and the relevant EPME are advised of the defects and the fault numbers for the work provided by OPHD.
DIST Level C Re-briefing – be aware and act

## Slide 34: DIST Level C Re-briefing – Procedure reminder
On arrival at the power distribution location the ECO must be contacted in order to seek permission to enter the distribution location.
On contacting the ECO you must clearly state your name, your employer’s name and the nature of your visit.
Upon entering be vigilant and aware of any untoward environmental conditions and hazards. Take the appropriate actions.
Complete the entry into the substation log book

## Slide 35
Upon leaving, the distribution location must be left safe and secure
On exiting, contact must be made with the ECO in order to request confirmation that all alarms have been cleared.
The ECO shall reset door alarms (where applicable).
Note: for non traction HV substations, there is no requirement to contact the ECO, however, authority to enter the location may be required from the Station Manager, or delegated responsible person, even if the person requiring entry is a permanent key holder.
DIST Level C Re-briefing – Procedure reminder

## Slide 36
Arc Flash PPE
Remember - PPE will not prevent a safety incident occurring but it can prevent or significantly reduce the severity of an injury.
ALWAYS wear the correct PPE for your task.
If you are only a DIST Level C you cannot work on the distribution equipment and so are not mandated to wear the Arc Flash PPE

## Slide 37: Level C Re-briefing – Further Discussion Points
Were you aware of the requirements and procedures of the Level C competence prior to the re-brief? Were there any surprises?
When was the last time you may have noticed water ingress or increased levels of condensation in distribution locations? Was this reported and action taken?
Have either yourself or your team had to invoke either the work-safe or close call procedure when accessing a distribution location? What were the outcomes?

## Slide 38: Safety Hour and Level C Briefing – Your views
Feedback from this briefing is greatly appreciated and can be directed to the Network Rail M&EE Distribution Team via:
Kyle.Windsor@networkrail.co.uk