## Slide 1
NR/L3/ELP/SAI25 Module D Distribution System Interfaces Detailed Briefing Level A (DIST AC-i) competent persons

## Slide 2
Purpose of this briefing
This Detailed Briefing has been developed to brief Level A (DIST AC-i) competent people on the following standard:
Level 3
NR/L3/ELP/SAI25 Module D Distribution System Interfaces
This briefing is designed to give Level A persons working in overhead line electrified areas an awareness of the SAI25 standard, in particular Module D, and a technical understanding of the requirements of this standard which are relevant to them.
Except where stated otherwise all red, amber or green (RAG) standard excerpts shown within this brief are taken from NR/L3/ELP/SAI25 Module D
It is the duty of those briefed to read and familiarise themselves with the standard and
to cascade as necessary all relevant information to those under your supervision who
are required to use the standard.
This briefing is not a substitute for reading the standard

## Slide 3
Aim of this briefing
The new NR/L3/ELP/SAI25 standard replaces NR/L3/ELP/29987 and among many other additions and changes introduces a new module (Module D) in Issue 2 which promotes the safe operation and effective management of Distribution System Interfaces.
The objective of this brief is to provide Level A persons with:
An introduction to the purpose of Single Approach to Isolations (SAI)
An awareness of the risk assessment process introduced in SAI25 Module 2 and the ways in which Level A persons may be called upon to support this
An overview of the general principles and requirements of SAI25 Module D
An overview of the new processes within Module D for working on lineside track feeder disconnectors and an understanding of the application and use of the new High Voltage Isolation and Earthing Certificate (HVIEC) introduced in NR/L3/ELP/21067 within these processes
An understanding of the new process in Module D for working on cabled circuits forming part of the OLE
An overview of the process in Module D for work on or work affected by traction power auxiliary supply transformers
An awareness of the requirements in Module D relating to work on structure mounted harmonic dampers and cable sealing ends

## Slide 4
Single Approach to Isolations
The creation of a Single Approach to Isolations standard aims to achieve improved identification of electrical hazards and an increased focus on mitigating those that remain. It increases the emphasis on the isolation and earthing of all exposed live overhead line equipment and distribution equipment thus demonstrating improving compliance with The Electricity at Work Regulations 1989.

## Slide 5
Scope of NR/L3/ELP/SAI25
SAI25 applies to all those required to work on or near Overhead Line Equipment (OLE), including persons who:
Assess electrical risk
Mitigate electrical risk through measures such as isolating, earthing, implementing control measures and issuing of formal safety assurance documents
Install, test, operate, maintain, repair and dismantle OLE and traction return systems
Work on rail vehicles or other equipment within 2.75 metres (9 feet) of overhead line equipment normally energised at 25 kV a.c.
Work on or about any future sections of electrification on Network Rail controlled infrastructure and areas required to adopt a process for securing points of disconnection to form points of isolation to implement a Supplementary Isolation Process
Work on or near the interface between OLE and traction distribution equipment

## Slide 6
Module 2 of SAI25 introduces a new Electrical Safe System of Work (ESSOW) hierarchy. This hierarchy is designed to provide a consistent approach to the assessment and management of electrical risk when working on or about OLE.
The electrical risk assessment principles are based on this structured hierarchy and the defined ESSOW categories present differing levels of electrical risk. The hierarchy prioritises implementation of the electrical safe systems of work that present less electrical risk.
An ESSOW is an integral part of the overall Safe System of Work (SSOW) that is implemented. The
ESSOW hierarchy shall be applied in
an order of priority where Category A
is considered the most preferred
option from an electrical risk
perspective and Category E the last
and least preferred.
Risk assessment
ESSOW Categorisation |  | Description
Category L | Low Electrical Risk Working | Specifically listed and approved tasks that do not require an Earthed Isolation. Entry within 2.75 m of exposed Live parts is only permitted for specifically listed and approved tasks.
Category A | Working with an Earthed Isolation in place for all Overhead Line Equipment (OLE) | Working where all OLE is under an Earthed Isolation within the Overhead Line Permit (OLP) along-track limits when visualised across all tracks. There are no residual electrical hazards within the OLP along-track limits when visualised across all tracks
Category B | Working with an Earthed Isolation in place for some OLE | Working where the OLE on some tracks is under an Earthed Isolation. Live OLE or other residual electrical hazards remain within the OLP along-track limits when visualised across all tracks
Category C |  | Not used
Category D | Working with the OLE Live | Working where the OLE is Live and no Earthed Isolation is in place. Excludes all Low Electrical Risk Working (category L) and Live Working (category E) tasks
Category E | Live Working on the OLE | Working within the Live Zone of the OLE. Live Working is restricted to specifically listed approved tasks using product accepted insulated tools

## Slide 7
Risk assessment cont.
As part of this risk assessment process there is often a requirement for an ERAS to carry out a site visit. This site visit can be needed in order to determine the electrical risk control measures at the relevant location(s). The ERAF will record the ESSOW categorisation decision and the control measures adopted.
ERAS is a role with a specific ERAS competence requirement. In the vast majority of cases the prerequisite competence for an ERAS will be Nominated Person.
Where work is not categorised as ESSOW category L and the work presents the risk of entering within 2.75m of exposed Live parts an electrical risk assessment shall be carried out by an Electrical Risk Assessor (ERAS) and an Electrical Risk Assessment Form (ERAF) completed.
NR/L3/ELP/SAI25 Module 2 states the following:

## Slide 8
Risk assessment cont.
In order to determine the appropriate electrical risk control measures at or near locations with exposed live distribution equipment the ERAS will need to consult a competent person. This person will require sufficient site-specific and technical knowledge of the electrical risks present and the risk mitigation measures most appropriate to deploy for the location.
The person likely to have such knowledge in most circumstances will be a Level A person.
As part of this consultation and risk assessment process the ERAS may wish to engage the
support of a Level A person, this may include conducting a joint site visit where appropriate
or necessary. There are numerous sequences detailed within Module D where a Level A
person will be required to engage collaboratively in the risk assessment and mitigation
process with the ERAS.
When work is to be undertaken on OLE in the proximity of high voltage distribution equipment and there is a foreseeable risk of persons tools, equipment or materials coming within 2.75 m of exposed live distribution equipment an electrical risk assessment shall be carried out in accordance with the requirements of Module 2.
NR/L3/ELP/SAI25 Module D goes on to state the following:

## Slide 9
SAI25 Module D
Different routes and regions are working with a large variety of equipment types, many of which are operated and secured differently. From tin huts to structure mounted equipment, classic systems to autotransformer fed systems, the equipment we operate and maintain looks different wherever you go.
Due to the different types of equipment found across the network, various methods of working on or near the interface between distribution and overhead line equipment have been adopted. The addition of Module D within NR/L3/ELP/SAI25 consolidates existing requirements and introduces new standardised approaches for working on or near these interfaces.

## Slide 10
Definitions
What is a distribution system interface?
It exists at or near the point of interaction between OLE and traction power distribution systems. A distribution system interface can be defined by many factors such as; physical proximity of equipment types, physical connection between equipment types, procedural arrangements for the isolation of equipment, and the procedural arrangements for working on equipment.
In summary, a distribution system interface is where either OLE or traction power distribution equipment affects or has the potential to affect the other, physically or procedurally.
SAI25 Module D also introduces the following new or unfamiliar terms which will be explained later in this briefing:
Integral Disconnector
Distribution Earth

## Slide 11
An example of a distribution system interface would be the location of this 25kV structure mounted harmonic damper
Visualisation
Work taking place on the highlighted earth wire forming part of the OLE would encroach within 2.75m of the damper
The damper is located lineside however it is fed directly from the nearby switching station, not connected directly to OLE, therefore it is defined as distribution equipment
The distribution system interface at this location is defined by the proximity of distribution equipment to OLE
The procedure for mitigating the risk at this
particular interface may require isolation of the
damper and the issue of a Permit to Work in
accordance with NR/L3/ELP/21067 prior to
work beginning on the highlighted earth wire

## Slide 12
General principles and requirements
Where identified as a requirement in the completed electrical risk assessment, the high voltage distribution equipment shall be Isolated and Earthed and a Permit to Work on the high voltage distribution equipment (Form 21067/P) shall first be issued in accordance with the requirements of NR/L3/ELP/21067. The electrical risk assessment shall determine the appropriate Electrical Safe System of Work ESSOW) along with the relevant electrical risk control measures to be implemented.
risers; bushings; cable sealing ends; bare feeders to bushings; OLE derived auxiliary supplies, related transformers and voltage regulators; Structure Mounted Outdoor Switchgear (SMOS)
Distribution equipment that might be in proximity to OLE equipment include:
There are further references within SAI25, particularly within Modules 7 and 11, where the
process requirements regarding issue of Permits to Work to Nominated Persons can be found

## Slide 13
Work on lineside track feeder disconnectors
Where a lineside disconnector is opened as part of maintenance or repair work involving the disconnector, it shall not be used as point of isolation. In this case the associated high voltage distribution equipment circuit breaker or integral disconnector forming part of the distribution equipment shall be used as the point of isolation.
Differing requirements apply to distribution equipment with no integral disconnector available to provide a point of isolation and distribution equipment that does incorporate an integral disconnector that can be used as a point of isolation.
Definition clarification:
The term ‘integral disconnector forming part of the distribution equipment’ refers exclusively to a disconnector, the function of which is central to the operation and purpose of disconnecting a circuit as a whole.
It doesn’t necessarily mean a disconnector which is integral to an individual switch housing,
mechanism or component.
A detached and mechanically separate disconnector forming part of a distribution SMOS
track feeder circuit assembly, for example, would still be defined as an integral disconnector
forming part of the distribution equipment for the purpose of this standard.

## Slide 14
Work on lineside track feeder disconnectors cont.
Examples of switchgear where the integral disconnector forming part of the distribution equipment is integral to the housing and mechanism of individual outgoing circuits:
Switchgear & Cowens K11
25kV oil filled switchgear
Siemens 8DA11 25kV gas insulated switchgear

## Slide 15
Work on lineside track feeder disconnectors cont.
Examples of switchgear with detached and mechanically separate disconnectors forming part of the track feeder circuit assemblies which would still be defined as integral disconnectors for the purpose of this standard:
ABB 25kV structure mounted switchgear (SMOS)
ABB 25kV SMOS Lite switchgear

## Slide 16
Differing requirements for work on lineside track feeder disconnectors
Module D introduces three new formal processes for working on lineside track feeder disconnectors, they are covered in detail in clause 4. These three processes follow two distinct pathways based primarily upon the absence or presence of integral disconnectors forming part of the distribution equipment. There is a potential requirement for collaborative working with Level A persons in order to facilitate an Earthed Isolation within Processes 1 and 3 and a certain requirement within Process 2.
To work on a lineside track feeder disconnector a point of isolation is required to be established on distribution equipment
Distribution equipment comprises of circuit breaker only
Distribution equipment comprises of circuit breaker and integral disconnector
Integral disconnector is not shown on OLE isolation diagrams
Process 2
Integral disconnector is shown on OLE isolation diagrams
Process 3
Process 1

## Slide 17
Differing requirements for work on lineside track feeder disconnectors cont.
The requirements of 4.2 shall apply in the case of electrification systems where the distribution system does not incorporate an integral disconnector and the circuit breaker is used as a point of isolation. In this case the circuit breaker shall be used as the point of isolation and a Circuit Main Earth (CME), in the form of duplicate portable earths, shall be applied between the circuit breaker and the lineside track feeder disconnector to be maintained prior to issuing an Overhead Line Permit (OLP).
Clause 4.2 covers the first of these three processes. There are still areas in the UK where sections of OLE are fed by traction distribution equipment utilising only circuit breakers with no disconnector. There is also equipment in use on the network which houses non-operable disconnectors.
Clause 4.2 details the sequence to be used to implement an Earthed Isolation using only circuit breakers as points of isolation. This sequence will not involve Level A persons however there is a caveat:
In some cases, it might not be practicable to apply a CME between the circuit breaker and lineside disconnector. Where this is the case, a different point(s) of isolation and associated earthing location(s) relevant to the distribution equipment might be required necessitating a High Voltage Isolation and Earthing Certificate (HVIEC) to be issued in accordance with the requirements of 4.3.

## Slide 18
Differing requirements for work on lineside track feeder disconnectors cont.
This is an example of an electrification system where a section of OLE is fed by traction distribution equipment utilising only circuit breakers with no disconnectors and where the requirements set out in Clause 4.2 would apply
Note that while disconnectors exist between bus sections and on the interconnecting
feed, there are
none on the
outgoing
circuits

## Slide 19
Differing requirements for work on lineside track feeder disconnectors cont.
The requirements of 4.4 shall apply in the case of electrification systems where an integral disconnector is available as part of distribution equipment to be used as a point of isolation and the integral disconnector is identified on the isolation diagrams and instructions.
Clause 4.4 is the third of these three processes which details the sequence for implementing an Earthed Isolation where there is an integral disconnector forming part of the distribution system and it is identified and available as a remotely operable point of isolation. Where this is the case the sequence as described in 4.2 will be followed but with the disconnector used as the point of isolation and not the circuit breaker.
This sequence will not normally involve Level A persons however given the requirement to follow the sequence described in 4.2, naturally the same caveat as the one detailed in 4.2 exists in regard to the location of the application of CMEs.
There is one clear exception within clause 4.4 which states as follows:
If a Supplementary Isolation Processes (SIP) is in place the requirements of section 4.3 shall apply.

## Slide 20
Differing requirements for work on lineside track feeder disconnectors cont.
This is an example of an electrification system where the OLE is fed by traction distribution equipment where integral disconnectors are available and identified and where the requirements set out in 4.4 would apply
The disconnectors are displayed on the route isolation diagram as shown

## Slide 21
Differing requirements for work on lineside track feeder disconnectors cont.
The requirements of 4.3 shall apply in the case of electrification systems where an integral disconnector is available as part of distribution equipment to be used as a point of isolation and the integral disconnector is not identified on the isolation diagrams and instructions. In this case the integral disconnector shall be used as the point of isolation with a High Voltage Isolation and Earthing Certificate issued by the Distribution Level A to enable a Form B to be issued and an OLP to be implemented.
Clause 4.3 is the second of these three processes but the final of the three to be covered in this brief. It details the sequence for implementing an Earthed Isolation where there is an integral disconnector forming part of the distribution system but it is not identified as a point of isolation within the route isolation diagrams or it is identified but requires manual operation. This process is also to be followed where any of the caveats or exceptions within 4.2 or 4.4 are applicable.
This sequence will involve Level A persons operating distribution equipment to prepare a point(s)
of isolation and earthing for Nominated Persons to utilise as part of an Earthed Isolation. The
actions required to make high voltage equipment safe prior to and during the issue of safety
documentation applicable within NR/L3/ELP/21067 are still applicable throughout this
sequence.
The purpose and requirements for the issue and return of a High Voltage Isolation and
Earthing Certificate (HVIEC) are found in NR/L3/ELP/21067

## Slide 22
Differing requirements for work on lineside track feeder disconnectors cont.
This is an example of an electrification system where the OLE is fed by traction distribution equipment with available and operable integral disconnectors
Here however the integral disconnectors are not displayed on the route isolation diagrams. They cannot be used to implement an
Earthed Isolation
without
support from
Level A
persons

## Slide 23
Differing requirements for work on lineside track feeder disconnectors cont.
An overview of the sequence within the process detailed in clause 4.3 is as follows:
The Level A shall coordinate and carry out the necessary switching operations and reconfiguration activities to facilitate the safe disconnection of outgoing distribution circuits requiring isolation and earthing
The Level A shall open and secure the relevant integral disconnector(s).
If the disconnector incorporates an earth position or an earthing mechanism, the earth shall be applied
The Level A shall prepare and issue a HVIEC along with the securing key to the Nominated Person in accordance with NR/L3/ELP/21067
The Nominated Person will implement an Earthed Isolation utilising the distribution equipment integral disconnector as a point of isolation. The HVIEC will be endorsed on the Form B and any OLPs issued
Upon completion of work the Nominated Person will ensure all OLPs have been cancelled and will then cancel the Form B
The Nominated person will return the HVIEC along with the securing key to the Level A who shall then cancel it in accordance with NR/L3/ELP/21067
The Level A shall remove applied earths and securing locks and close the relevant integral disconnector(s)
The Level A shall coordinate and carry out the necessary switching operations and reconfiguration activities required to return the equipment to service
Where an integral earthing device is not available to be applied, a CME in the form of duplicated portable earths shall be applied between the circuit breaker and the lineside track feeder disconnector to be maintained
The track feeder disconnector to be maintained will be opened at this stage to facilitate issue of the High Voltage Isolation and Earthing Certificate (HVIEC) that covers the integral disconnector(s) providing a point(s) of isolation and the integral earth(s) where applied.

## Slide 24
Maintenance of cabled circuits forming part of the OLE
Overhead line equipment is not covered within the scope of NR/L3/ELP/21067, however there are elements of the overhead line system that require the specialist skills of distribution staff to conduct installation, maintenance or testing work upon it.
Where such work is to take place a process (Clause 5) has been developed to formalise a sequence for collaborative working between overhead line and distribution staff. A brief overview of the sequence is as follows:
ECO
B
NP
B
NP
OLP
COSS
OLP
A
OLP
A Form B shall be prepared and used to implement an Earthed Isolation and any required electrical risk control measures shall be implemented
The Nominated Person shall then issue an overhead line permit (OLP) to the COSS OLP and to the Distribution Level A responsible for the work on the affected equipment

## Slide 25
Maintenance of cabled circuits forming part of the OLE cont.
The ESSOW which is developed by the ERAS and implemented by the Nominated Person will include among the mitigation measures to be deployed; a separate Safe System of Work (SSOW) for which the Level A will be responsible for developing and implementing.
The requirements for the development, implementation and maintenance of a SSOW detailing suitable control measures for the work on or testing of conductors or earth screening forming part of a high voltage cable within an overhead line system are covered in NR/L3/ELP/21067.
An ESSOW shall be implemented in accordance with the requirements of Module 2. The Distribution Level A shall take account of and implement suitable control measures for the electrical risks related to the work on the cabled section including risks associated with induction and alternate current paths.
Typical tasks undertaken by persons with the relevant distribution equipment competencies in accordance with NR/L3/ELP/21067 include, cable spiking, jointing and pressure testing.

## Slide 26
Maintenance of cabled circuits forming part of the OLE cont.
Module D introduces the term distribution earth (DE) and calls for them to be applied prior to the issue of safety documentation in accordance with NR/L3/ELP/21067.
Definition clarification:
For the purpose of this standard, distribution earth is the term given to the dual portable earths applied on Overhead Line Equipment at either or both ends of the cabled circuit either by, or by arrangement of the Level A.
One or more distribution earths will be required to be applied as an essential part of mitigating
against the risk of impressed voltages. A distribution earth is by definition not a CME, nor is it
an Additional Earth, however the Level A may wish to use it as such.
Following receipt of the OLP, the Distribution Level A holding the OLP shall arrange for the application of distribution earths in the form of duplicate short portable earths at either end of the cabled circuit utilising the spigots provided at the respective cable sealing end locations…

## Slide 27
Maintenance of cabled circuits forming part of the OLE cont.
Part of the sequence developed for this work may involve the disconnection and reconnection of cable drapes forming the link between the overhead line and cabled parts of the electrification system. Where such work is required the Level A is responsible for coordinating and arranging for their removal.
The purpose of the Nominated Person issuing an OLP is to allow for a distribution safety document such as a Permit to Work or Sanction for Test to be issued in accordance with NR/L3/ELP/21067 under which this disconnection and reconnection of cable drapes can take place where required.
Where a Sanction for Test is issued the following shall be observed:
Where required in accordance with NR/L3/ELP/21067, the Distribution Level A shall not issue a Sanction for Test until the Nominated Person has confirmed that the cable sealing ends under test are identified as residual electrical hazards on all affected OLPs. Prior to undertaking testing, the Distribution Level A shall implement controls in accordance with NR/L3/ELP/21067 including segregating the testing area with suitable barriers and danger notices.

## Slide 28
Maintenance of cabled circuits forming part of the OLE cont.
Potential arrangements in place at a location where distribution staff are involved in such work:

## Slide 29
Maintenance of cabled circuits forming part of the OLE cont.
Pertinent points of consideration for the Level A person developing, implementing and maintaining a SSOW for work on a cabled section of ATF:
Which control measures are most suitable for mitigating the risk of alternate current paths?
  Is an isolation of additional or all lines required?
  Do one or more distribution earths require removal to facilitate work?
  Do one or more cable screens require earthing and/or bonding?
If disconnected drapes are to be relied upon for points of isolation, how are they secured and inadvertent reconnection prevented?
  Have the drapes been removed and retained or are they left tied up at high level?
  Is it suitable to incorporate assurance activities in to the SSOW where the site of work has been left unattended at any point?
  Are the lineside track feeder disconnectors for the section of ATF to be worked on more suitable for use as points of isolation?
  What barriers and warning notices may be required and where?

## Slide 30
25kV auxiliary supplies
Clause 6 of Module D introduces new steps for those who work on OLE to assess and mitigate against the risk of 25kV auxiliary supplies back-feeding the OLE from the LV side.
Example mitigation measures relevant to the risk of back-feeding the OLE from the low voltage side of the auxiliary supply transformer include: a) isolation of the OLE disconnector associated with the auxiliary power supply; b) isolation of the relevant low voltage circuit; c) validating that the design is such that the risk of back-feeding is suitably mitigated. The relevant isolation instructions should identify any isolation requirements applicable to mitigating the risk of back-feeding from 25 kV auxiliary supplies
Mitigation measures are likely to include collaboration or consultation with Level A persons.

## Slide 31
25kV auxiliary supplies cont.
Also introduced in clause 6 are steps for those who work on auxiliary supplies to assess and mitigate against the risk of coming within 2.75m of exposed live OLE.
The requirements for the issue of a distribution safety document such as a Permit to Work or
Sanction for Test in accordance with NR/L3/ELP/21067 apply when working on 25kV auxiliary
supplies. Where the OLE has been isolated to enable work on an auxiliary supply, the OLP shall
be endorsed on the Permit to Work.
Where work on an OLE derived auxiliary power supply transformer and associated equipment is required and the work presents a foreseeable risk of persons tools, equipment or materials coming within 2.75 m of exposed live equipment an electrical risk assessment shall be carried out and ESSOW implemented in accordance with the requirements of Module 2. Where identified as a requirement in the completed electrical risk assessment, the OLE shall be isolated and earthed as required to implement the identified ESSOW

## Slide 32
Isolating structure mounted harmonic dampers
The procedure for isolating structure mounted harmonic dampers depends on whether the they’re connected directly or indirectly to the OLE. The fundamental procedural principle remains unchanged from what was once found within NR/L3/ELP/29987 Module 7 and is now incorporated within clause 7 of Module D.
Where a damper is connected indirectly to the OLE at a switching station the isolation and earthing requirements and the requirements for the issue of distribution safety documentation such as a Permit to Work or Sanction for Test within NR/L3/ELP/21067 apply.
Where a damper is connected directly to the OLE it is to be treated as part of the OLE.

## Slide 33
Key takeaways
The new NR/L3/ELP/SAI25 standard replaces NR/L3/ELP/29987 and among many other additions and changes introduces a new module (Module D) in Issue 2 which promotes the safe operation and effective management of Distribution System Interfaces. These changes will in many cases require collaboration with competent Level A persons in order to identify and mitigate the risk of coming into contact with exposed live distribution equipment.
NR/L3/ELP/SAI25 Module 2 introduces a new ESSOW hierarchy designed to provide a consistent approach to the assessment and management of electrical risk when working on or about OLE
SAI25 Module D introduces the following:
  New processes within for working on lineside track feeder disconnectors
  A new process for working on cabled circuits forming part of the OLE
  New principles for work on or work affected by traction power auxiliary supply transformers
SAI25 Module D incorporates the following:
  The procedure for isolating structure mounted harmonic dampers

## Slide 34
Questions
Contact ESDSAISupport@networkrail.co.uk or visit Safety Central for further support

## Slide 35
To login to your Sentinel account scan this QR Code :
Or go to : https://mysentinel.me/Account/LogOn/
To register for a Sentinel account scan this QR code:
Or go to: https://mysentinel.me/Account/Register
If you are a Sentinel card holder you can register for a Sentinel account on the website using the link below.
You might be asked to prove you’ve received this brief. You can do this by logging into to the Sentinel website once registered with your login credentials and clicking:
My Profile
Events
Proof of briefing